TECHNICAL SERVICE REPORT

Water Analysis

| Customer: | Location: | Date: | PO#: |
| --- | --- | --- | --- |
| Chick-fil-A | # 259 | 3/21/07 | 274648 |
| Address: |  | Tested By: |  |
| Regency Square (AL) 301 Cox Creek Pkwy Florence, AL 35630 |  | AR |  |
| Phone: | Email: | Selecto Contact: |  |

| Recommendation: |  |
| --- | --- |

##### ANALYTICAL RESULTS

| Evaluation of: | Bathroom Water Sample | Drink Tower Water Sample | Recommended Max Levels |
| --- | --- | --- | --- |
| Fluoride, ppm | 0.9 | 0.9 | 2 ppm |
| Chloride, ppm | 63 | 59 | 250 ppm |
| Nitrite, ppm | ND | ND | 1 ppm as N |
| Nitrate, ppm | 0.4 | 0.4 | 10 ppm as N |
| Sulfate, ppm | 15 | 14 | 250 ppm |
| Sodium, ppm | 27 | 25 | 250 ppm |
| Ammonia as Chloramine | ND | ND | .5 ppm |
| Chlorine, ppm | Detected | Detected | Detectable |
| Alkalinity, ppm | 50 | 50 | 150 ppm |
| Total Dissolved Solids, ppm | 180 | 170 | 500 ppm |
| Hardness, ppm | 75 | 75 | 100 ppm |
| pH | 7.4 | 7.4 | 6.5 – 8.5 ppm |
| Turbidity | 0.00 | 0.00 | .05 NTU |

The information supplied is believed to be accurate and is only indicative of the water tested.  The testing laboratory is not state certified.

3980 Lakefield Court    Suwanee, GA 30024    678.475.0799    800.635.4017

www.selectoinc.com

sales@selectoinc.com