TECHNICAL SERVICE REPORT

Water Analysis

| Customer: | Location: | Date: | PO#: |
| --- | --- | --- | --- |
| Chick-fil-A | # 1402 | 11/17/05 | 229709 |
| Address: |  | Tested By: |  |
| Pensacola, FL 32503 |  | AR |  |
| Phone: | Email: | Selecto Contact: |  |
| 850-484-5521 |  | John Edmonds |  |

| Recommendation: |  |
| --- | --- |

##### ANALYTICAL RESULTS

| Evaluation of: | Unfiltered Water Sample | Filtered Water Sample | Recommended Max Levels |
| --- | --- | --- | --- |
| Fluoride, ppm | 0.4 | 0.3 | 2 ppm |
| Chloride, ppm | 28 | 25 | 250 ppm |
| Nitrite, ppm | ND | ND | 1 ppm as N |
| Nitrate, ppm | 2.0 | 2.0 | 10 ppm as N |
| Sulfate, ppm | 1.7 | 1.7 | 250 ppm |
| Sodium, ppm | 24 | 22 | 10 ppm |
| Ammonia as Chloramine | Must be tested on site | Must be tested on site | .5 ppm |
| Chlorine, ppm | Must be tested on site | Must be tested on site | Detectable |
| Alkalinity, ppm | 45 | 45 | 150 ppm |
| Total Dissolved Solids, ppm | 120 | 120 | 500 ppm |
| Hardness, ppm | 65 | 64 | 100 ppm |
| pH | 6.7 | 6.7 | 6.5 – 8.5 ppm |
| Turbidity | 1.11 | 1.82 | 0.5 NTU |

The information supplied is believed to be accurate and is only indicative of the water tested.  The testing laboratory is not state certified.

3980 Lakefield Court    Suwanee, GA 30024    678.475.0799    800.635.4017

www.selectoinc.com

sales@selectoinc.com